## ROI Calculator
Cooling Tower Gearbox Purge Mist: Cost Savings & ROI Calculator
Oil Mist Lubrication Institute ¦ theoilmistinstitute.org ¦ Keith Macaluso, CRL
HOW TO USE: Replace the yellow cells (blue text) with your own plant's numbers. Everything else calculates. The values shown are the worked example from the article (4-cell tower).
1. YOUR COOLING TOWER
Number of fan gearboxes (cells) | 4 | Count every cell, including spares and seasonal cells.
Oil per gearbox (gallons) | 30 | Right-angle CT fan reducers typically hold 10-30 gal (Mobil Productivity Pointer: Cooling Towers). Large refinery towers can hold more. Use your nameplate / OEM manual.
Gear oil price ($/gallon) | 35 | Assumption: premium synthetic gear oil, delivered. Use your purchase price.
Disposal cost ($/gallon), incl. absorbents, drums, manifest | 5 | Assumption. Contaminated oil, rags and absorbent pads leave as waste. Use your waste contractor rate.
2. WHAT ONE GEARBOX OIL CHANGE TAKES TODAY
Crew size (people) | 6 | Example: 2 mechanics inside the fan stack, 1 attendant/hole watch, 1 rigger/signal on the ground, 1 operator for LOTO and cell isolation, 1 safety/permit writer.
Hours per gearbox oil change (incl. permits, LOTO, drain, flush, fill) | 8 | Assumption. CCJ (St. Charles Energy Center) reports a single SAMPLING entry took at least 2 hours; a full drain/flush/fill takes far longer.
Fully burdened labor rate ($/hour) | 95 | Assumption: Gulf Coast contract craft rate. Use your own.
Crane cost per gearbox change ($) | 1500 | Assumption: operated crane day shared across cells, plus rigger. Set to 0 if drums go up by a fixed davit or elevator.
Scaffolding / temporary platform per change ($) | 3000 | Assumption: erect + inspect + dismantle inside the fan stack. Set to 0 if you have a permanent platform.
Permits, gas testing, rescue standby per change ($) | 500 | Confined space entry permit, atmospheric testing, fall protection, rescue plan, LOTO.
Lost cooling / production per change ($) | 0 | Conservative default is $0. In summer, a cell out of service can cost far more than everything else on this sheet.
3. RISK (EXPECTED COST PER OIL CHANGE)
Chance of an oil spill per oil change | 2% | Assumption. Hoses, drums and drain valves at height, over a water basin.
Cost of a spill (cleanup, reporting, basin treatment) | 25000 | Assumption. Oil in the basin goes into the circulating water system.
Chance of a recordable injury per oil change | 1% | Assumption. Work at height, confined space, suspended loads, wet surfaces.
Cost per medically consulted work injury | 48000 | National Safety Council, Injury Facts: $48,000 per medically consulted injury (2024).
4. OIL CHANGES AND FAILURES
Oil changes per gearbox per year TODAY | 2 | Ehlert: CT gearbox oil typically changed twice a year without purge mist.
Oil change interval WITH purge mist (years) | 2 | Ehlert: once every 2-3 years with purge mist, confirmed by oil sampling. Field users report much longer. 2 years is conservative.
Gearbox failures per year TODAY (whole tower) | 0.5 | Assumption: one failure every 2 years. The Pennsylvania refinery case had 2 failures/yr on ONE cell.
Cost per gearbox failure ($) | 50000 | Pennsylvania refinery case: about $50,000 per repair (Macaluso, OMLI).
Failure reduction with purge mist | 40% | Users report about 40% fewer failures in wet-sump equipment purged with oil mist (Macaluso, Oil Mist 101). The PA refinery saw 100%.
5. OIL MIST SYSTEM
Installed cost of purge mist to the tower ($) | 60000 | Assumption: header extension from an existing generator, drops, reclassifiers, vent collection, and drain/sample lines piped outside the fan stack. Get a quote for your tower.
Annual mist oil + PM for the tower ($/yr) | 2000 | Assumption.
Oil samples per gearbox per year | 4 | Sampling is what lets you safely stretch the interval.
Cost per oil sample incl. labor ($) | 150 | Assumption. Pipe a sample point outside the fan stack so sampling needs no entry.
Evaluation period (years) | 10
RESULTS: COST OF ONE GEARBOX OIL CHANGE
New oil | 1050
Disposal of old oil and waste | 150
Labor (crew x hours x rate) | 4560
Crane | 1500
Scaffolding | 3000
Permits and safety standby | 500
Lost cooling / production | 0
Spill risk (expected) | 500
Injury risk (expected) | 480
TOTAL COST PER GEARBOX OIL CHANGE | 11740
RESULTS: ANNUAL COST, TODAY vs. PURGE MIST
Oil changes per year, whole tower, TODAY | 8
Oil changes per year, whole tower, WITH MIST | 2
Oil change cost TODAY ($/yr) | 93920
Gearbox failure cost TODAY ($/yr) | 25000
TOTAL TODAY ($/yr) | 118920
Oil change cost WITH MIST ($/yr) | 23480
Gearbox failure cost WITH MIST ($/yr) | 15000
Oil sampling ($/yr) | 2400
Mist oil + PM ($/yr) | 2000
TOTAL WITH MIST ($/yr) | 42880
THE BOTTOM LINE
Annual savings ($/yr) | 76040
Simple payback (months) | 9.4687
Net savings over evaluation period ($) | 700400
Return on investment over evaluation period | 1167%
Oil changes avoided per year | 6
High-risk work hours avoided per year (at height / confined space) | 288
Drum lifts avoided per year (full drums up + used oil down) | 12 | A full 55-gal drum of gear oil weighs roughly 450 lb.
Gallons of oil bought and disposed avoided per year | 180

## Sources
Sources behind the default values (everything else is a labeled assumption you should replace):
Ehlert, D. (2011). Getting the Facts on Oil Mist Lubrication. Texas A&M Turbomachinery Laboratory Tutorial. https://turbolab.tamu.edu/wp-content/uploads/2018/08/Tutorial-08.pdf (CT gearbox oil changes 2x/yr -> once every 2-3 yrs with purge mist; oil sampling; vent back-pressure / false-high sight glass)
Mobil Productivity Pointer: Cooling Towers. https://www.global.mobil.com/-/media/files/global/us/industrial/productivity-pointer/cooling-towers-productivy.pdf (10-30 gal per right-angle drive)
Combined Cycle Journal, Cooling-tower fan gearbox mod facilitates oil sampling, recharge (St. Charles Energy Center). https://www.ccj-online.com/?p=16692 (entry, LOTO, shroud removal, fall protection; 2+ hours per sampling entry)
National Safety Council, Injury Facts: Work Injury Costs. https://injuryfacts.nsc.org/work/costs/work-injury-costs/ ($48,000 per medically consulted injury, 2024)
Macaluso, K. Extend Asset Life with Oil Mist for Storage Preservation. OMLI. https://www.theoilmistinstitute.org/articles/extend-asset-life-storage-preservation.html (PA refinery: 2 failures/yr x $50,000, eliminated; payback < 1 yr)
Macaluso, K. My Oil Mist Lubrication Elevator Talk (Oil Mist 101). OMLI. https://www.theoilmistinstitute.org/articles/oil-mist-101.html (40% fewer failures in purged wet-sump equipment; oil change intervals x8)
Disclaimer: This calculator is an educational screening tool. Results depend entirely on the inputs. Verify with your own cost data and a site assessment.